{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["Best interm. coolpack","Best inerm. log","Best inerm. kol","Best intermediate","Confirm Kolsaker","Kolsaker sheet"],"not_rendered":{"charts":0,"images":14,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Best interm. coolpack","index":0,"n_rows":94,"n_cols":18,"rows_kept":94,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
["Best intermediat pressure for",null,null,"R744","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",0,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",-33,"˚C","Temperature",48.7,"˚C","Temperature",33.700000000000003,"˚C","Temperature",113.5,"˚C"]
["Pressure",12.07,"bar","Pressure",{"$f":"B11","v":12.07},"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",85,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",80,"%",null,null,null,"Isentropic efficiency",{"$f":"E13","v":80},"%"]
[null,null,null,"Heat loss",5,"%"]
[null,null,null,"mR744",2.3300000000000001E-2,"kg/s",null,null,null,null,null,null,"Gas cooler output"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Temperature",10,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Pressure",null,"bar"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C",20,"˚C"]
["Comp",2.68,"kW",2.71,"kW",2.73,"kW",2.73,"kW",2.76,"kW",2.78,"kW",2.79,"kW",2.79,"kW"]
["Gas cooler",7.28,"kW",7.3,"kW",7.32,"kW",7.33,"kW",7.34,"kW",7.35,"kW",7.35,"kW",7.36,"kW"]
["COP",{"$f":"B21/(B20)","v":2.716417910447761},null,{"$f":"D21/(D20)","v":2.6937269372693726},null,{"$f":"F21/(F20)","v":2.6813186813186816},null,{"$f":"H21/(H20)","v":2.6849816849816852},null,{"$f":"J21/(J20)","v":2.6594202898550727},null,{"$f":"L21/(L20)","v":2.6438848920863309},null,{"$f":"N21/(N20)","v":2.6344086021505375},null,{"$f":"P21/(P20)","v":2.6379928315412187}]
[]
[]
[]
[]
[]
[]
[]
[]
["Best intermediat pressure for",null,null,"R717","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",null,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",-33,"˚C","Temperature",159.30000000000001,"˚C","Temperature",17,"˚C","Temperature",59.6,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"E37","v":70},"%"]
[null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,"mR717 total",5.0000000000000001E-3,"kg/s",null,null,null,null,null,null,"Temperature",30,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C",20,"˚C"]
["Comp",2.6,"kW",2.5,"kW",2.4,"kW",2.2000000000000002,"kW",2.1,"kW",2,"kW",1.8,"kW",1.7,"kW"]
["Gas cooler",9.4,"kW",9.4,"kW",9.5,"kW",9.5,"kW",9.5,"kW",9.6,"kW",9.6,"kW",9.6,"kW"]
["COP",{"$f":"B44/(B43)","v":3.6153846153846154},null,{"$f":"D44/(D43)","v":3.7600000000000002},null,{"$f":"F44/(F43)","v":3.9583333333333335},null,{"$f":"H44/(H43)","v":4.3181818181818175},null,{"$f":"J44/(J43)","v":4.5238095238095237},null,{"$f":"L44/(L43)","v":4.8},null,{"$f":"N44/(N43)","v":5.333333333333333},null,{"$f":"P44/(P43)","v":5.6470588235294121}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Best intermediat pressure for",null,null,"R290","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",null,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"E61","v":70},"%"]
[null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,"mR290 total",0.02,"kg/s",null,null,null,null,null,null,"Temperature",30,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C",20,"˚C"]
["Comp",2.5,"kW",2.4,"kW",2.2000000000000002,"kW",2.1,"kW",1.9,"kW",1.8,"kW",1.7,"kW",1.6,"kW"]
["Gas cooler",9.6,"kW",9.4,"kW",9.1999999999999993,"kW",9,"kW",8.8000000000000007,"kW",8.6,"kW",8.4,"kW",8.1999999999999993,"kW"]
["COP",{"$f":"B68/(B67)","v":3.84},null,{"$f":"D68/(D67)","v":3.916666666666667},null,{"$f":"F68/(F67)","v":4.1818181818181808},null,{"$f":"H68/(H67)","v":4.2857142857142856},null,{"$f":"J68/(J67)","v":4.6315789473684212},null,{"$f":"L68/(L67)","v":4.7777777777777777},null,{"$f":"N68/(N67)","v":4.9411764705882355},null,{"$f":"P68/(P67)","v":5.1249999999999991}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"The same effect on bouth the compressors"]
["Best intermediat pressure for",null,null,"R410A","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",null,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"E86","v":70},"%"]
[null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,"mR410A total",2.9000000000000001E-2,"kg/s",null,null,null,null,null,null,"Temperature",30,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C",20,"˚C"]
["Comp",2.2000000000000002,"kW",2.1,"kW",1.9,"kW",1.8,"kW",1.7,"kW",1.6,"kW",1.5,"kW",1.4,"kW"]
["Gas cooler",8.5,"kW",8.1999999999999993,"kW",8,"kW",7.8,"kW",7.6,"kW",7.5,"kW",7.3,"kW",7.1,"kW"]
["COP",{"$f":"B93/(B92)","v":3.8636363636363633},null,{"$f":"D93/(D92)","v":3.9047619047619042},null,{"$f":"F93/(F92)","v":4.2105263157894735},null,{"$f":"H93/(H92)","v":4.333333333333333},null,{"$f":"J93/(J92)","v":4.4705882352941178},null,{"$f":"L93/(L92)","v":4.6875},null,{"$f":"N93/(N92)","v":4.8666666666666663},null,{"$f":"P93/(P92)","v":5.0714285714285712}]

{"sheet":"Best inerm. log","index":1,"n_rows":197,"n_cols":35,"rows_kept":197,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Best intermediat pressure for",null,null,"R717","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",null,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",-33,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"E20","v":70},"%"]
[null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,"mR717 total",5.0000000000000001E-3,"kg/s",null,null,null,null,null,null,"Temperature",28,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",1.82,null,1.71,null,1.63,null,1.54,null,1.46,null,1.41,null,1.42]
["Gas cooler",7.99,null,8.0299999999999994,null,8.0399999999999991,null,8.0399999999999991,null,8.07,null,8.1199999999999992,null,8.24]
["COP",{"$f":"B27/B26","v":4.3901098901098905},null,{"$f":"D27/D26","v":4.6959064327485374},null,{"$f":"F27/F26","v":4.9325153374233128},null,{"$f":"H27/H26","v":5.2207792207792201},null,{"$f":"J27/J26","v":5.5273972602739727},null,{"$f":"L27/L26","v":5.7588652482269502},null,{"$f":"N27/N26","v":5.802816901408451}]
[]
[]
["Refrigerant","R717","Temp",-15,"˚C","Refrigerant","R717","Temp",-10,"˚C","Refrigerant","R717","Temp",-5,"˚C","Refrigerant","R717","Temp",0,"˚C","Refrigerant","R717","Temp",5,"˚C","Refrigerant","R717","Temp",10,"˚C","Refrigerant","R717","Temp",15,"˚C"]
["xf","hA",1419.5,"kJ/kg",null,"xf","hA",1419.5,"kJ/kg",null,"xf","hA",1419.5,"kJ/kg",null,"xf","hA",1419.5,"kJ/kg",null,"xf","hA",1419.5,"kJ/kg",null,"xf","hA",1419.5,"kJ/kg",null,"xf","hA",1419.5,"kJ/kg"]
["(hC-hF)/(hC-hG)","hB",1589.35,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",1632.5,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",1675,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",1719.3,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",1762,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",1806,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",1849,"kJ/kg"]
[{"$f":"(C34-C37)/(C34-C38)","v":0.91987447698744762},"hC",1565,"kJ/kg",null,{"$f":"(H34-H37)/(H34-H38)","v":0.93778234086242296},"hC",1616,"kJ/kg",null,{"$f":"(M34-M37)/(M34-M38)","v":0.95338294993234096},"hC",1655,"kJ/kg",null,{"$f":"(R34-R37)/(R34-R38)","v":0.96931818181818175},"hC",1696,"kJ/kg",null,{"$f":"(W34-W37)/(W34-W38)","v":0.9848944591029023},"hC",1739,"kJ/kg",null,{"$f":"(AB34-AB37)/(AB34-AB38)","v":0.99941406249999998},"hC",1781,"kJ/kg",null,{"$f":"(AG34-AG37)/(AG34-AG38)","v":0.99943037974683535},"hC",1825,"kJ/kg"]
[null,"hD",1843,"kJ/kg",null,null,"hD",1851,"kJ/kg",null,null,"hD",1853,"kJ/kg",null,null,"hD",1854,"kJ/kg",null,null,"hD",1860,"kJ/kg",null,null,"hD",1870,"kJ/kg",null,null,"hD",1894,"kJ/kg"]
["COP two stage","hE",245.9,"kJ/kg",null,"COP two stage","hE",245.9,"kJ/kg",null,"COP two stage","hE",245.9,"kJ/kg",null,"COP two stage","hE",245.9,"kJ/kg",null,"COP two stage","hE",245.9,"kJ/kg",null,"COP two stage","hE",245.9,"kJ/kg",null,"COP two stage","hE",245.9,"kJ/kg"]
["(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"C36","v":245.9},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"H36","v":245.9},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"M36","v":245.9},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"R36","v":245.9},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"W36","v":245.9},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AB36","v":245.9},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AG36","v":245.9},"kJ/kg"]
[{"$f":"(C35-C36)/(A34*(C33-C32)+(C35-C34))","v":3.6779142854782179},"hG",131,"kJ/kg",null,{"$f":"(H35-H36)/(F34*(H33-H32)+(H35-H34))","v":3.6920269542008133},"hG",155,"kJ/kg",null,{"$f":"(M35-M36)/(K34*(M33-M32)+(M35-M34))","v":3.6393541259540343},"hG",177,"kJ/kg",null,{"$f":"(R35-R36)/(P34*(R33-R32)+(R35-R34))","v":3.5846952676676564},"hG",200,"kJ/kg",null,{"$f":"(W35-W36)/(U34*(W33-W32)+(W35-W34))","v":3.5217263683435811},"hG",223,"kJ/kg",null,{"$f":"(AB35-AB36)/(Z34*(AB33-AB32)+(AB35-AB34))","v":3.4171900597538301},"hG",245,"kJ/kg",null,{"$f":"(AG35-AG36)/(AE34*(AG33-AG32)+(AG35-AG34))","v":3.3077417157297404},"hG",245,"kJ/kg"]
[null,"hH",{"$f":"C38","v":131},"kJ/kg",null,null,"hH",{"$f":"H38","v":155},"kJ/kg",null,null,"hH",{"$f":"M38","v":177},"kJ/kg",null,null,"hH",{"$f":"R38","v":200},"kJ/kg",null,null,"hH",{"$f":"W38","v":223},"kJ/kg",null,null,"hH",{"$f":"AB38","v":245},"kJ/kg",null,null,"hH",{"$f":"AG38","v":245},"kJ/kg"]
[]
[null,"mR717",5.0000000000000001E-3,"kg/s",null,null,"mR717",5.0000000000000001E-3,"kg/s",null,null,"mR717",5.0000000000000001E-3,"kg/s",null,null,"mR717",5.0000000000000001E-3,"kg/s",null,null,"mR717",5.0000000000000001E-3,"kg/s",null,null,"mR717",5.0000000000000001E-3,"kg/s",null,null,"mR717",5.0000000000000001E-3,"kg/s"]
[]
[null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp"]
[null,"1.",{"$f":"(C41/2)*(C33-C32)","v":0.42462499999999981},"kW",null,null,"1.",{"$f":"(H41/2)*(H33-H32)","v":0.53249999999999997},"kW",null,null,"1.",{"$f":"(M41/2)*(M33-M32)","v":0.63875000000000004},"kW",null,null,"1.",{"$f":"(R41/2)*(R33-R32)","v":0.74949999999999994},"kW",null,null,"1.",{"$f":"(W41/2)*(W33-W32)","v":0.85625000000000007},"kW",null,null,"1.",{"$f":"(AB41/2)*(AB33-AB32)","v":0.96625000000000005},"kW",null,null,"1.",{"$f":"(AG41/2)*(AG33-AG32)","v":1.07375},"kW"]
[null,"2.",{"$f":"C41*(C35-C34)","v":1.3900000000000001},"kW",null,null,"2.",{"$f":"H41*(H35-H34)","v":1.175},"kW",null,null,"2.",{"$f":"M41*(M35-M34)","v":0.99},"kW",null,null,"2.",{"$f":"R41*(R35-R34)","v":0.79},"kW",null,null,"2.",{"$f":"W41*(W35-W34)","v":0.60499999999999998},"kW",null,null,"2.",{"$f":"AB41*(AB35-AB34)","v":0.44500000000000001},"kW",null,null,"2.",{"$f":"AG41*(AG35-AG34)","v":0.34500000000000003},"kW"]
[null,"Tot",{"$f":"SUM(C44:C45)","v":1.8146249999999999},"kW",null,null,"Tot",{"$f":"SUM(H44:H45)","v":1.7075},"kW",null,null,"Tot",{"$f":"SUM(M44:M45)","v":1.6287500000000001},"kW",null,null,"Tot",{"$f":"SUM(R44:R45)","v":1.5394999999999999},"kW",null,null,"Tot",{"$f":"SUM(W44:W45)","v":1.4612500000000002},"kW",null,null,"Tot",{"$f":"SUM(AB44:AB45)","v":1.4112500000000001},"kW",null,null,"Tot",{"$f":"SUM(AG44:AG45)","v":1.41875},"kW"]
[]
[null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler"]
[null,null,{"$f":"C41*(C35-C36)","v":7.9855},"kW",null,null,null,{"$f":"H41*(H35-H36)","v":8.0254999999999992},"kW",null,null,null,{"$f":"M41*(M35-M36)","v":8.035499999999999},"kW",null,null,null,{"$f":"R41*(R35-R36)","v":8.0404999999999998},"kW",null,null,null,{"$f":"W41*(W35-W36)","v":8.0704999999999991},"kW",null,null,null,{"$f":"AB41*(AB35-AB36)","v":8.1204999999999998},"kW",null,null,null,{"$f":"AG41*(AG35-AG36)","v":8.240499999999999},"kW"]
[]
[null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect"]
[null,null,{"$f":"C49/C46","v":4.4006337397533928},null,null,null,null,{"$f":"H49/H46","v":4.7001464128843331},null,null,null,null,{"$f":"M49/M46","v":4.9335379892555631},null,null,null,null,{"$f":"R49/R46","v":5.2227996102630732},null,null,null,null,{"$f":"W49/W46","v":5.5230111206159096},null,null,null,null,{"$f":"AB49/AB46","v":5.7541186891054021},null,null,null,null,{"$f":"AG49/AG46","v":5.8082819383259903}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Best intermediat pressure for",null,null,"R290","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",null,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",-33,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"E68","v":70},"%"]
[null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,"mR290 total",0.02,"kg/s",null,null,null,null,null,null,"Temperature",28,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.5,null,2.5099999999999998,null,2.48,null,2.5099999999999998,null,2.56,null,2.62,null,2.79]
["Condenser",8.5,null,8.5399999999999991,null,8.48,null,8.48,null,8.48,null,8.5440000000000005,null,8.5399999999999991]
["COP",{"$f":"B75/B74","v":3.4},null,{"$f":"D75/D74","v":3.402390438247012},null,{"$f":"F75/F74","v":3.4193548387096775},null,{"$f":"H75/H74","v":3.378486055776893},null,{"$f":"J75/J74","v":3.3125},null,{"$f":"L75/L74","v":3.2610687022900762},null,{"$f":"N75/N74","v":3.0609318996415769}]
[]
[]
["Refrigerant","R290","Temp",-15,"˚C",null,null,"Temp",-10,"˚C","Refrigerant",null,"Temp",-5,"˚C","Refrigerant",null,"Temp",0,"˚C","Refrigerant",null,"Temp",5,"˚C","Refrigerant",null,"Temp",10,"˚C","Refrigerant",null,"Temp",15,"˚C"]
["xf","hA",537.1,"kJ/kg",null,"xf","hA",537.1,"kJ/kg",null,"xf","hA",537.1,"kJ/kg",null,"xf","hA",537.1,"kJ/kg",null,"xf","hA",537.1,"kJ/kg",null,"xf","hA",537.1,"kJ/kg",null,"xf","hA",537.1,"kJ/kg"]
["(hC-hF)/(hC-hG)","hB",585.5,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",596.79999999999995,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",607.79999999999995,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",618.6,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",629,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",639.1,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",649,"kJ/kg"]
[{"$f":"(C82-C85)/(C82-C86)","v":0.84875621890547259},"hC",566,"kJ/kg",null,{"$f":"(H82-H85)/(H82-H86)","v":0.87673267326732673},"hC",579,"kJ/kg",null,{"$f":"(M82-M85)/(M82-M86)","v":0.90597014925373132},"hC",589,"kJ/kg",null,{"$f":"(R82-R85)/(R82-R86)","v":0.93799999999999994},"hC",600,"kJ/kg",null,{"$f":"(W82-W85)/(W82-W86)","v":0.96783919597989942},"hC",610,"kJ/kg",null,{"$f":"(AB82-AB85)/(AB82-AB86)","v":1},"hC",623,"kJ/kg",null,{"$f":"(AG82-AG85)/(AG82-AG86)","v":1.0312020460358056},"hC",628,"kJ/kg"]
[null,"hD",650,"kJ/kg",null,null,"hD",652,"kJ/kg",null,null,"hD",649,"kJ/kg",null,null,"hD",649,"kJ/kg",null,null,"hD",649,"kJ/kg",null,null,"hD",652,"kJ/kg",null,null,"hD",652,"kJ/kg"]
["COP two stage","hE",224.8,"kJ/kg",null,"COP two stage","hE",224.8,"kJ/kg",null,"COP two stage","hE",224.8,"kJ/kg",null,"COP two stage","hE",224.8,"kJ/kg",null,"COP two stage","hE",224.8,"kJ/kg",null,"COP two stage","hE",224.8,"kJ/kg",null,"COP two stage","hE",224.8,"kJ/kg"]
["(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"C84","v":224.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"H84","v":224.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"M84","v":224.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"R84","v":224.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"W84","v":224.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AB84","v":224.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AG84","v":224.8},"kJ/kg"]
[{"$f":"(C83-C84)/(A82*(C81-C80)+(C83-C82))","v":3.3994297769702451},"hG",164,"kJ/kg",null,{"$f":"(H83-H84)/(F82*(H81-H80)+(H83-H82))","v":3.408303767111251},"hG",175,"kJ/kg",null,{"$f":"(M83-M84)/(K82*(M81-M80)+(M83-M82))","v":3.419531275379025},"hG",187,"kJ/kg",null,{"$f":"(R83-R84)/(P82*(R81-R80)+(R83-R82))","v":3.3815077283633728},"hG",200,"kJ/kg",null,{"$f":"(W83-W84)/(U82*(W81-W80)+(W83-W82))","v":3.3155020985085395},"hG",212,"kJ/kg",null,{"$f":"(AB83-AB84)/(Z82*(AB81-AB80)+(AB83-AB82))","v":3.2610687022900762},"hG",{"$f":"AB85","v":224.8},"kJ/kg",null,{"$f":"(AG83-AG84)/(AE82*(AG81-AG80)+(AG83-AG82))","v":3.064749088475156},"hG",237,"kJ/kg"]
[null,"hH",{"$f":"C86","v":164},"kJ/kg",null,null,"hH",{"$f":"H86","v":175},"kJ/kg",null,null,"hH",{"$f":"M86","v":187},"kJ/kg",null,null,"hH",{"$f":"R86","v":200},"kJ/kg",null,null,"hH",{"$f":"W86","v":212},"kJ/kg",null,null,"hH",224.8,"kJ/kg",null,null,"hH",{"$f":"AG86","v":237},"kJ/kg"]
[]
[null,"mR290",0.02,"kg/s",null,null,"mR290",0.02,"kg/s",null,null,"mR290",0.02,"kg/s",null,null,"mR290",0.02,"kg/s",null,null,"mR290",0.02,"kg/s",null,null,"mR290",0.02,"kg/s",null,null,"mR290",0.02,"kg/s"]
[]
[null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp"]
[null,"1.",{"$f":"(C89*A82)*(C81-C80)","v":0.82159601990049702},"kW",null,null,"1.",{"$f":"(H89*F82)*(H81-H80)","v":1.046818811881187},"kW",null,null,"1.",{"$f":"(M89*K82)*(M81-M80)","v":1.2810417910447749},"kW",null,null,"1.",{"$f":"(R89*P82)*(R81-R80)","v":1.52894},"kW",null,null,"1.",{"$f":"(W89*U82)*(W81-W80)","v":1.7788884422110549},"kW",null,null,"1.",{"$f":"(AB89*Z82)*(AB81-AB80)","v":2.04},"kW",null,null,"1.",{"$f":"(AG89*AE82)*(AG81-AG80)","v":2.3078301790281324},"kW"]
[null,"2.",{"$f":"C89*(C83-C82)","v":1.68},"kW",null,null,"2.",{"$f":"H89*(H83-H82)","v":1.46},"kW",null,null,"2.",{"$f":"M89*(M83-M82)","v":1.2},"kW",null,null,"2.",{"$f":"R89*(R83-R82)","v":0.98},"kW",null,null,"2.",{"$f":"W89*(W83-W82)","v":0.78},"kW",null,null,"2.",{"$f":"AB89*(AB83-AB82)","v":0.57999999999999996},"kW",null,null,"2.",{"$f":"AG89*(AG83-AG82)","v":0.48},"kW"]
[null,"Tot",{"$f":"SUM(C92:C93)","v":2.501596019900497},"kW",null,null,"Tot",{"$f":"SUM(H92:H93)","v":2.5068188118811872},"kW",null,null,"Tot",{"$f":"SUM(M92:M93)","v":2.4810417910447748},"kW",null,null,"Tot",{"$f":"SUM(R92:R93)","v":2.5089399999999999},"kW",null,null,"Tot",{"$f":"SUM(W92:W93)","v":2.5588884422110549},"kW",null,null,"Tot",{"$f":"SUM(AB92:AB93)","v":2.62},"kW",null,null,"Tot",{"$f":"SUM(AG92:AG93)","v":2.7878301790281323},"kW"]
[]
[null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler"]
[null,null,{"$f":"C89*(C83-C84)","v":8.5039999999999996},"kW",null,null,null,{"$f":"H89*(H83-H84)","v":8.5440000000000005},"kW",null,null,null,{"$f":"M89*(M83-M84)","v":8.484},"kW",null,null,null,{"$f":"R89*(R83-R84)","v":8.484},"kW",null,null,null,{"$f":"W89*(W83-W84)","v":8.484},"kW",null,null,null,{"$f":"AB89*(AB83-AB84)","v":8.5440000000000005},"kW",null,null,null,{"$f":"AG89*(AG83-AG84)","v":8.5440000000000005},"kW"]
[]
[null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect"]
[null,null,{"$f":"C97/C94","v":3.3994297769702451},null,null,null,null,{"$f":"H97/H94","v":3.408303767111251},null,null,null,null,{"$f":"M97/M94","v":3.4195312753790255},null,null,null,null,{"$f":"R97/R94","v":3.3815077283633728},null,null,null,null,{"$f":"W97/W94","v":3.3155020985085395},null,null,null,null,{"$f":"AB97/AB94","v":3.2610687022900762},null,null,null,null,{"$f":"AG97/AG94","v":3.0647490884751565}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Best intermediat pressure for",null,null,"R410A","at an evaporation temperature of ",null,null,-35,"˚C",", and it is ",null,"˚C"]
[]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",-35,"˚C","Temperature",-33,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"E116","v":70},"%"]
[null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,"mR410A total",0.03,"kg/s",null,null,null,null,null,null,"Temperature",28,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.2200000000000002,"kW",2.2999999999999998,"kW",2.5299999999999998,"kW",2.4900000000000002,"kW",2.44,"kW",2.5099999999999998,"kW",2.54,"kW"]
["Condenser",7.92,"kW",7.49,"kW",8.2200000000000006,"kW",8.1,"kW",8.0399999999999991,"kW",8.01,"kW",7.98,"kW"]
["COP",{"$f":"B123/B122","v":3.5675675675675671},null,{"$f":"D123/D122","v":3.2565217391304353},null,{"$f":"F123/F122","v":3.2490118577075102},null,{"$f":"H123/H122","v":3.2530120481927707},null,{"$f":"J123/J122","v":3.2950819672131146},null,{"$f":"L123/L122","v":3.1912350597609564},null,{"$f":"N123/N122","v":3.1417322834645671}]
[]
[]
["Refrigerant","R410A","Temp",-15,"˚C","Refrigerant",null,"Temp",-10,"˚C","Refrigerant",null,"Temp",-5,"˚C","Refrigerant",null,"Temp",0,"˚C","Refrigerant",null,"Temp",5,"˚C","Refrigerant",null,"Temp",10,"˚C","Refrigerant",null,"Temp",15,"˚C"]
["xf","hA",408.6,"kJ/kg",null,"xf","hA",408.6,"kJ/kg",null,"xf","hA",408.8,"kJ/kg",null,"xf","hA",408.6,"kJ/kg",null,"xf","hA",408.8,"kJ/kg",null,"xf","hA",408.6,"kJ/kg",null,"xf","hA",408.6,"kJ/kg"]
["(hC-hF)/(hC-hG)","hB",438,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",446,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",453,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",460,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",467,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",473.1,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",480,"kJ/kg"]
[{"$f":"(C130-C133)/(C130-C134)","v":0.84645669291338588},"hC",431,"kJ/kg",null,{"$f":"(H130-H133)/(H130-H134)","v":0.87777777777777777},"hC",437,"kJ/kg",null,{"$f":"(M130-M133)/(M130-M134)","v":0.90909090909090906},"hC",445,"kJ/kg",null,{"$f":"(R130-R133)/(R130-R134)","v":0.93253968253968256},"hC",451,"kJ/kg",null,{"$f":"(W130-W133)/(W130-W134)","v":0.97199999999999998},"hC",458,"kJ/kg",null,{"$f":"(AB130-AB133)/(AB130-AB134)","v":1},"hC",463,"kJ/kg",null,{"$f":"(AG130-AG133)/(AG130-AG134)","v":1.0323886639676114},"hC",470,"kJ/kg"]
[null,"hD",480,"kJ/kg",null,null,"hD",486,"kJ/kg",null,null,"hD",489,"kJ/kg",null,null,"hD",486,"kJ/kg",null,null,"hD",483,"kJ/kg",null,null,"hD",482,"kJ/kg",null,null,"hD",481,"kJ/kg"]
["COP two stage","hE",216,"kJ/kg",null,"COP two stage","hE",215.8,"kJ/kg",null,"COP two stage","hE",215,"kJ/kg",null,"COP two stage","hE",216,"kJ/kg",null,"COP two stage","hE",215,"kJ/kg",null,"COP two stage","hE",215,"kJ/kg",null,"COP two stage","hE",215,"kJ/kg"]
["(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"C132","v":216},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"H132","v":215.8},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"M132","v":215},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"R132","v":216},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"W132","v":215},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AB132","v":215},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AG132","v":215},"kJ/kg"]
[{"$f":"(C131-C132)/(A130*(C129-C128)+(C131-C130))","v":3.5730804070975655},"hG",177,"kJ/kg",null,{"$f":"(H131-H132)/(F130*(H129-H128)+(H131-H130))","v":3.3020123292507408},"hG",185,"kJ/kg",null,{"$f":"(M131-M132)/(K130*(M129-M128)+(M131-M130))","v":3.2548596112311019},"hG",192,"kJ/kg",null,{"$f":"(R131-R132)/(P130*(R129-R128)+(R131-R130))","v":3.2556581654624628},"hG",199,"kJ/kg",null,{"$f":"(W131-W132)/(U130*(W129-W128)+(W131-W130))","v":3.285505526514521},"hG",208,"kJ/kg",null,{"$f":"(AB131-AB132)/(Z130*(AB129-AB128)+(AB131-AB130))","v":3.1976047904191618},"hG",{"$f":"AB133","v":215},"kJ/kg",null,{"$f":"(AG131-AG132)/(AE130*(AG129-AG128)+(AG131-AG130))","v":3.1400305868858736},"hG",223,"kJ/kg"]
[null,"hH",{"$f":"C134","v":177},"kJ/kg",null,null,"hH",{"$f":"H134","v":185},"kJ/kg",null,null,"hH",{"$f":"M134","v":192},"kJ/kg",null,null,"hH",{"$f":"R134","v":199},"kJ/kg",null,null,"hH",{"$f":"W134","v":208},"kJ/kg",null,null,"hH",215,"kJ/kg",null,null,"hH",{"$f":"AG134","v":223},"kJ/kg"]
[]
[null,"mR410A",0.03,"kg/s",null,null,"mR410A",0.03,"kg/s",null,null,"mR410A",0.03,"kg/s",null,null,"mR410A",0.03,"kg/s",null,null,"mR410A",0.03,"kg/s",null,null,"mR410A",0.03,"kg/s",null,null,"mR410A",0.03,"kg/s"]
[]
[null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp"]
[null,"1.",{"$f":"(C137*A130)*(C129-C128)","v":0.74657480314960578},"kW",null,null,"1.",{"$f":"(H137*F130)*(H129-H128)","v":0.98486666666666611},"kW",null,null,"1.",{"$f":"(M137*K130)*(M129-M128)","v":1.2054545454545451},"kW",null,null,"1.",{"$f":"(R137*P130)*(R129-R128)","v":1.4379761904761899},"kW",null,null,"1.",{"$f":"(W137*U130)*(W129-W128)","v":1.6971119999999995},"kW",null,null,"1.",{"$f":"(AB137*Z130)*(AB129-AB128)","v":1.9349999999999998},"kW",null,null,"1.",{"$f":"(AG137*AE130)*(AG129-AG128)","v":2.2113765182186227},"kW"]
[null,"2.",{"$f":"C137*(C131-C130)","v":1.47},"kW",null,null,"2.",{"$f":"H137*(H131-H130)","v":1.47},"kW",null,null,"2.",{"$f":"M137*(M131-M130)","v":1.3199999999999998},"kW",null,null,"2.",{"$f":"R137*(R131-R130)","v":1.05},"kW",null,null,"2.",{"$f":"W137*(W131-W130)","v":0.75},"kW",null,null,"2.",{"$f":"AB137*(AB131-AB130)","v":0.56999999999999995},"kW",null,null,"2.",{"$f":"AG137*(AG131-AG130)","v":0.32999999999999996},"kW"]
[null,"Tot",{"$f":"SUM(C140:C141)","v":2.216574803149606},"kW",null,null,"Tot",{"$f":"SUM(H140:H141)","v":2.4548666666666659},"kW",null,null,"Tot",{"$f":"SUM(M140:M141)","v":2.525454545454545},"kW",null,null,"Tot",{"$f":"SUM(R140:R141)","v":2.4879761904761901},"kW",null,null,"Tot",{"$f":"SUM(W140:W141)","v":2.4471119999999997},"kW",null,null,"Tot",{"$f":"SUM(AB140:AB141)","v":2.5049999999999999},"kW",null,null,"Tot",{"$f":"SUM(AG140:AG141)","v":2.5413765182186228},"kW"]
[]
[null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler"]
[null,null,{"$f":"C137*(C131-C132)","v":7.92},"kW",null,null,null,{"$f":"H137*(H131-H132)","v":8.1059999999999999},"kW",null,null,null,{"$f":"M137*(M131-M132)","v":8.2199999999999989},"kW",null,null,null,{"$f":"R137*(R131-R132)","v":8.1},"kW",null,null,null,{"$f":"W137*(W131-W132)","v":8.0399999999999991},"kW",null,null,null,{"$f":"AB137*(AB131-AB132)","v":8.01},"kW",null,null,null,{"$f":"AG137*(AG131-AG132)","v":7.9799999999999995},"kW"]
[]
[null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect"]
[null,null,{"$f":"C145/C142","v":3.5730804070975655},null,null,null,null,{"$f":"H145/H142","v":3.3020123292507408},null,null,null,null,{"$f":"M145/M142","v":3.2548596112311019},null,null,null,null,{"$f":"R145/R142","v":3.2556581654624628},null,null,null,null,{"$f":"W145/W142","v":3.2855055265145201},null,null,null,null,{"$f":"AB145/AB142","v":3.1976047904191618},null,null,null,null,{"$f":"AG145/AG142","v":3.1400305868858736}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Refrigerant","R744"]
["Evaporator input",null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",85,"bar"]
[null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,"Isentropic efficiency",80,"%",null,null,null,"Isentropic efficiency",{"$f":"E163","v":80},"%"]
[null,null,null,"Heat loss",5,"%"]
[null,null,null,"mR744",2.3300000000000001E-2,"kg/s",null,null,null,null,null,null,"Gas cooler output"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Temperature",10,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Pressure",null,"bar"]
[]
[]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.48,"kW",2.4300000000000002,"kW",2.44,"kW",2.63,"kW",2.31,"kW",2.52,"kW",2.84,"kW"]
["Condenser",7.39,"kW",7.32,"kW",7.32,"kW",7.46,"kW",7.08,"kW",7.25,"kW",7.55,"kW"]
["COP",{"$f":"B172/B171","v":2.979838709677419},null,{"$f":"D172/D171","v":3.0123456790123457},null,{"$f":"F172/F171","v":3},null,{"$f":"H172/H171","v":2.8365019011406845},null,{"$f":"J172/J171","v":3.0649350649350651},null,{"$f":"L172/L171","v":2.876984126984127},null,{"$f":"N172/N171","v":2.658450704225352}]
[]
[]
["Refrigerant","R410A","Temp",-15,"˚C","Refrigerant","R410A","Temp",-10,"˚C","Refrigerant","R410A","Temp",-5,"˚C","Refrigerant","R410A","Temp",0,"˚C","Refrigerant","R410A","Temp",5,"˚C","Refrigerant","R410A","Temp",10,"˚C","Refrigerant","R410A","Temp",15,"˚C"]
["xf","hA",439,"kJ/kg",null,"xf","hA",439,"kJ/kg",null,"xf","hA",439,"kJ/kg",null,"xf","hA",439,"kJ/kg",null,"xf","hA",439,"kJ/kg",null,"xf","hA",439,"kJ/kg",null,"xf","hA",439,"kJ/kg"]
["(hC-hF)/(hC-hG)","hB",471,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",480,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",488,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",497,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",505,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",512,"kJ/kg",null,"(hC-hF)/(hC-hG)","hB",521,"kJ/kg"]
[{"$f":"(C179-C182)/(C179-C183)","v":0.8},"hC",461,"kJ/kg",null,{"$f":"(H179-H182)/(H179-H183)","v":0.83561643835616439},"hC",469,"kJ/kg",null,{"$f":"(M179-M182)/(M179-M183)","v":0.87197231833910038},"hC",477,"kJ/kg",null,{"$f":"(R179-R182)/(R179-R183)","v":0.91228070175438591},"hC",485,"kJ/kg",null,{"$f":"(W179-W182)/(W179-W183)","v":0.9537366548042705},"hC",493,"kJ/kg",null,{"$f":"(AB179-AB182)/(AB179-AB183)","v":1},"hC",501,"kJ/kg",null,{"$f":"(AG179-AG182)/(AG179-AG183)","v":1},"hC",509,"kJ/kg"]
[null,"hD",542,"kJ/kg",null,null,"hD",539,"kJ/kg",null,null,"hD",539,"kJ/kg",null,null,"hD",545,"kJ/kg",null,null,"hD",529,"kJ/kg",null,null,"hD",536,"kJ/kg",null,null,"hD",549,"kJ/kg"]
["COP two stage","hE",225,"kJ/kg",null,"COP two stage","hE",225,"kJ/kg",null,"COP two stage","hE",225,"kJ/kg",null,"COP two stage","hE",225,"kJ/kg",null,"COP two stage","hE",225,"kJ/kg",null,"COP two stage","hE",225,"kJ/kg",null,"COP two stage","hE",225,"kJ/kg"]
["(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"C181","v":225},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"H181","v":225},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"M181","v":225},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"R181","v":225},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"W181","v":225},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"AB181","v":225},"kJ/kg",null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",225,"kJ/kg"]
[{"$f":"(C180-C181)/(A179*(C178-C177)+(C180-C179))","v":2.9737335834896812},"hG",166,"kJ/kg",null,{"$f":"(H180-H181)/(F179*(H178-H177)+(H180-H179))","v":3.0116936013664435},"hG",177,"kJ/kg",null,{"$f":"(M180-M181)/(K179*(M178-M177)+(M180-M179))","v":2.9982819004823895},"hG",188,"kJ/kg",null,{"$f":"(R180-R181)/(P179*(R178-R177)+(R180-R179))","v":2.8340584213797388},"hG",200,"kJ/kg",null,{"$f":"(W180-W181)/(U179*(W178-W177)+(W180-W179))","v":3.0723636886778878},"hG",212,"kJ/kg",null,{"$f":"(AB180-AB181)/(Z179*(AB178-AB177)+(AB180-AB179))","v":2.8796296296296298},"hG",225,"kJ/kg",null,{"$f":"(AG180-AG181)/(AE179*(AG178-AG177)+(AG180-AG179))","v":2.6557377049180326},"hG",225,"kJ/kg"]
[null,"hH",{"$f":"C183","v":166},"kJ/kg",null,null,"hH",{"$f":"H183","v":177},"kJ/kg",null,null,"hH",{"$f":"M183","v":188},"kJ/kg",null,null,"hH",{"$f":"R183","v":200},"kJ/kg",null,null,"hH",{"$f":"W183","v":212},"kJ/kg",null,null,"hH",{"$f":"AB183","v":225},"kJ/kg",null,null,"hH",{"$f":"AG183","v":225},"kJ/kg"]
[]
[null,"mR717",2.3300000000000001E-2,"kg/s",null,null,"mR717",2.3300000000000001E-2,"kg/s",null,null,"mR717",2.3300000000000001E-2,"kg/s",null,null,"mR717",2.3300000000000001E-2,"kg/s",null,null,"mR717",2.3300000000000001E-2,"kg/s",null,null,"mR717",2.3300000000000001E-2,"kg/s",null,null,"mR717",2.3300000000000001E-2,"kg/s"]
[]
[null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp",null,null,null,null,"Effect of comp"]
[null,"1.",{"$f":"(C186*A179)*(C178-C177)","v":0.59648000000000001},"kW",null,null,"1.",{"$f":"(H186*F179)*(H178-H177)","v":0.79826438356164398},"kW",null,null,"1.",{"$f":"(M186*K179)*(M178-M177)","v":0.99553079584775095},"kW",null,null,"1.",{"$f":"(R186*P179)*(R178-R177)","v":1.2328561403508771},"kW",null,null,"1.",{"$f":"(W186*U179)*(W178-W177)","v":1.4666562277580073},"kW",null,null,"1.",{"$f":"(AB186*Z179)*(AB178-AB177)","v":1.7009000000000001},"kW",null,null,"1.",{"$f":"(AG186*AE179)*(AG178-AG177)","v":1.9106000000000001},"kW"]
[null,"2.",{"$f":"C186*(C180-C179)","v":1.8873000000000002},"kW",null,null,"2.",{"$f":"H186*(H180-H179)","v":1.631},"kW",null,null,"2.",{"$f":"M186*(M180-M179)","v":1.4446000000000001},"kW",null,null,"2.",{"$f":"R186*(R180-R179)","v":1.3980000000000001},"kW",null,null,"2.",{"$f":"W186*(W180-W179)","v":0.83879999999999999},"kW",null,null,"2.",{"$f":"AB186*(AB180-AB179)","v":0.8155},"kW",null,null,"2.",{"$f":"AG186*(AG180-AG179)","v":0.93200000000000005},"kW"]
[null,"Tot",{"$f":"SUM(C189:C190)","v":2.4837800000000003},"kW",null,null,"Tot",{"$f":"SUM(H189:H190)","v":2.4292643835616441},"kW",null,null,"Tot",{"$f":"SUM(M189:M190)","v":2.4401307958477512},"kW",null,null,"Tot",{"$f":"SUM(R189:R190)","v":2.6308561403508772},"kW",null,null,"Tot",{"$f":"SUM(W189:W190)","v":2.3054562277580075},"kW",null,null,"Tot",{"$f":"SUM(AB189:AB190)","v":2.5164},"kW",null,null,"Tot",{"$f":"SUM(AG189:AG190)","v":2.8426},"kW"]
[]
[null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Effect of gas cooler"]
[null,null,{"$f":"C186*(C180-C181)","v":7.3861000000000008},"kW",null,null,null,{"$f":"H186*(H180-H181)","v":7.3162000000000003},"kW",null,null,null,{"$f":"M186*(M180-M181)","v":7.3162000000000003},"kW",null,null,null,{"$f":"R186*(R180-R181)","v":7.4560000000000004},"kW",null,null,null,{"$f":"W186*(W180-W181)","v":7.0832000000000006},"kW",null,null,null,{"$f":"AB186*(AB180-AB181)","v":7.2463000000000006},"kW",null,null,null,{"$f":"AG186*(AG180-AG181)","v":7.5492000000000008},"kW"]
[]
[null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect",null,null,null,null,"COP-comp effect"]
[null,null,{"$f":"C194/C191","v":2.9737335834896812},null,null,null,null,{"$f":"H194/H191","v":3.011693601366443},null,null,null,null,{"$f":"M194/M191","v":2.9982819004823891},null,null,null,null,{"$f":"R194/R191","v":2.8340584213797393},null,null,null,null,{"$f":"W194/W191","v":3.0723636886778878},null,null,null,null,{"$f":"AB194/AB191","v":2.8796296296296298},null,null,null,null,{"$f":"AG194/AG191","v":2.6557377049180331}]

{"sheet":"Best inerm. kol","index":2,"n_rows":77,"n_cols":20,"rows_kept":77,"cut":false,"hidden":false,"merged":[]}
[]
["Refrigerant",null,"R744"]
["Two-stage Compression",null,null,null,null,null,null,null,null,null,"Refrigerant"]
["Evaporation temperature",null,-35,"˚C",null,null,"Fixed value",null,null,null,"xf","hA",{"$f":"r_hgastp(C2,C6,C5*100000)/1000","v":439.15192062485249},"kJ/kg",null,null,"xf","hA",538,"kJ/kg"]
["Evaporation pressure",null,{"$f":"r_psatgasT(C2,C4)/100000","v":12.0324759881664},"bar",null,null,null,null,null,null,"(hC-hF)/(hC-hG)","hB",{"$f":"C8+(C17-C8)/C15","v":532.59868209214142},"kJ/kg",null,null,"(hC-hF)/(hC-hG)","hB",629,"kJ/kg"]
["Temperature in to compressor",null,{"$f":"C4+2","v":-33},"˚C",null,null,null,null,null,null,{"$f":"(M6-M9)/(M6-M10)","v":0.74580911740528844},"hC",{"$f":"r_hgastp(C2,C23,C13*100000)/1000","v":521.0600163815825},"kJ/kg",null,null,{"$f":"(S6-S9)/(S6-S10)","v":0.96},"hC",610,"kJ/kg"]
["1. Compressor",null,null,null,null,null,null,null,null,null,null,"hD",{"$f":"C24+(C34-C24)/C32","v":547.004785761211},"kJ/kg",null,null,null,"hD",653,"kJ/kg"]
["Enthalpy input compressor",null,{"$f":"r_hgastp(C2,C6,C5*100000)/1000","v":439.15192062485249},"kJ/kg",null,null,null,null,null,null,"COP two stage","hE",{"$f":"R_hsatliqT(C2,C28-G19)/1000","v":225.55950670395399},"kJ/kg",null,null,"COP two stage","hE",226,"kJ/kg"]
["Entropy",null,{"$f":"R_SgasTP(C2,C6,C5*100000)","v":2033.7129582427001},"J/kgK",null,null,null,null,null,null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"M8","v":225.55950670395399},"kJ/kg",null,null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"S8","v":226},"kJ/kg"]
["Specific volume",null,{"$f":"R_vgasTP(C2,C6,C5*100000)","v":3.2461387899901141E-2},"m3/kg",null,null,null,null,null,null,{"$f":"(M7-M8)/(K6*(M5-M4)+(M7-M6))","v":3.3610547357844385},"hG",{"$f":"R_HsatliqP(C2,C5*100000)/1000","v":124.8453512864556},"kJ/kg",null,null,{"$f":"(S7-S8)/(Q6*(S5-S4)+(S7-S6))","v":3.2755446455968085},"hG",210,"kJ/kg"]
[null,null,null,null,null,null,null,null,null,null,null,"hH",{"$f":"M10","v":124.8453512864556},"kJ/kg",null,null,null,"hH",{"$f":"S10","v":210},"kJ/kg"]
["Intermediat temperature",null,15,"˚C"]
["Intermediat pressure",null,{"$f":"r_psatgasT(C2,C12)/100000","v":50.859803234991311},"bar",null,null,null,null,null,null,null,"mR717",5.0000000000000001E-3,"kg/s",null,null,null,"mR717",0.02,"kg/s"]
["Intermediat pressure ratio",null,{"$f":"C13/C5","v":4.2268776006709254}]
["Isentropic efficiency",null,0.7,null,null,null,null,null,null,null,null,null,"Effect of comp",null,null,null,null,null,"Effect of comp"]
[null,null,null,null,null,null,null,null,null,null,null,"1.",{"$f":"(M13*K6)*(M5-M4)","v":0.34846723347150632},"kW",null,null,null,"1.",{"$f":"(S13*Q6)*(S5-S4)","v":1.7471999999999999},"kW"]
["Isentropic entalpy",null,{"$f":"R_hgasSP(C2,C9,C13*100000)/1000","v":504.5646536519547},"kJ/kg",null,null,null,null,null,null,null,"2.",{"$f":"M13*(M7-M6)","v":0.12972384689814248},"kW",null,null,null,"2.",{"$f":"S13*(S7-S6)","v":0.86},"kW"]
["Real entropy",null,{"$f":"C8+(C17-C8)/C15","v":532.59868209214142},"kJ/kg",null,null,null,null,null,null,null,"Tot",{"$f":"SUM(M16:M17)","v":0.4781910803696488},"kW",null,null,null,"Tot",{"$f":"SUM(S16:S17)","v":2.6071999999999997},"kW"]
["Temperature out of compressor",null,{"$f":"R_tgasHP(C2,C18*1000,C13*100000)","v":92.414286188597714},"˚C","Subcooling of condenser",null,18,"K"]
["Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(C2,C12)/1000","v":417.72014872753522},"kJ/kg","Enthalpy out of the condenser",null,{"$f":"R_hsatliqT(C2,C28-G19)/1000","v":225.55950670395399},"kJ/kg",null,null,null,null,"Effect of gas cooler",null,null,null,null,null,"Effect of gas cooler"]
["2. Compressor",null,null,null,null,null,null,null,null,null,null,null,{"$f":"M13*(M7-M8)","v":1.6072263952862853},"kW",null,null,null,null,{"$f":"S13*(S7-S8)","v":8.5400000000000009},"kW"]
["Intermediat cooling",null,10,"K","Enthalpy in to evaporator",null,225,"kJ/kg"]
["Temperature in to 2. compressor",null,{"$f":"C19-C22","v":82.414286188597714},"˚C","Moist vapor - xf",null,{"$f":"(C24-G20)/(C24-G22)","v":0.99811015782950974},null,null,null,null,null,"COP-comp effect",null,null,null,null,null,"COP-comp effect"]
["Enthalpy input in 2. compressor",null,{"$f":"r_hgastp(C2,C23,C13*100000)/1000","v":521.0600163815825},"kJ/kg","Cooling capacity",null,{"$f":"G26*(C8-G22)","v":4.989739750559063},"kW",null,null,null,null,{"$f":"M21/M18","v":3.3610547357844389},null,null,null,null,null,{"$f":"S21/S18","v":3.2755446455968094}]
["Entropy",null,{"$f":"R_SgasTP(C2,C23,C13*100000)","v":2080.48427708283},"J/kgK","Cooling COP",null,{"$f":"G24/G34","v":1.7963515009384237}]
["Specific volume",null,{"$f":"R_vgasTP(C2,C23,C13*100000)","v":1.122280975506664E-2},"m3/kg","Refrigerant mass flow",null,2.3300000000000001E-2,"kg/s"]
[null,null,null,null,"Volume flow",null,{"$f":"G28/3600","v":2.166666666666667E-3},"m3/s"]
["Condensating temperature",null,28,"˚C","Volume flow",null,{"$f":"G30*G29","v":7.8000000000000007},"m3/h"]
["Condensating pressure",null,{"$f":"r_psatgasT(C2,C28)/100000","v":68.892048623022362},"bar","Volumetric efficiency",null,0.65]
["Pressure ration",null,{"$f":"C29/C13","v":1.3545480761047253},null,"Cylinder volume",null,12,"m3/h"]
["Pressure ration TOTAL",null,{"$f":"C29/C5","v":5.7255089219189585}]
["Isentropic efficiency",null,0.7,null,"Compressor effect 1. compressor",null,{"$f":"(G26*G23)*(C18-C8)","v":2.1731947707967945},"kW"]
[null,null,null,null,"Compressor effect 2. compressor",null,{"$f":"G26*(C35-C24)","v":0.60451312654534395},"kW"]
["Isentropic entalpy",null,{"$f":"R_hgasSP(C2,C25,C29*100000)/1000","v":539.22135494732242},"kJ/kg","Compressor effect TOTAL",null,{"$f":"G33+G32","v":2.7777078973421383},"kW"]
["Real entropy",null,{"$f":"C24+(C34-C24)/C32","v":547.004785761211},"kJ/kg","Over heating heat",null,{"$f":"(G26*(C35-C37))+((G26/2)*(C18-C20))","v":5.1845148072262592},"kW"]
["Temperature out of compressor",null,{"$f":"R_tgasHP(C2,C35*1000,C29*100000)","v":115.28772484168989},"˚C","Heating capacity",null,{"$f":"(G26*(C35-G20))","v":7.4896750020340894},"kW"]
["Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(C2,C28)/1000","v":381.93268732650728},"kJ/kg","Heating COP",null,{"$f":"G36/G34","v":2.6963508327137697}]
[]
[]
["Refrigerant","R744"]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.74,"kW",2.77,"kW",2.78,"kW",2.79,"kW",2.79,"kW",2.79,"kW",2.78,"kW"]
["Gas cooler",7.47,"kW",7.49,"kW",7.51,"kW",7.51,"kW",7.51,"kW",7.5,"kW",7.49,"kW"]
["COP",{"$f":"B43/(B42)","v":2.7262773722627736},null,{"$f":"D43/(D42)","v":2.7039711191335742},null,{"$f":"F43/(F42)","v":2.7014388489208634},null,{"$f":"H43/(H42)","v":2.6917562724014337},null,{"$f":"J43/(J42)","v":2.6917562724014337},null,{"$f":"L43/(L42)","v":2.6881720430107525},null,{"$f":"N43/(N42)","v":2.6942446043165469}]
[]
[]
[]
[]
["Refrigerant","R717"]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.65,"kW",2.64,"kW",2.64,"kW",2.63,"kW",2.62,"kW",2.61,"kW",2.61,"kW"]
["Condenser",8.5399999999999991,"kW",8.56,"kW",8.56,"kW",8.56,"kW",8.5500000000000007,"kW",8.5399999999999991,"kW",8.52,"kW"]
["COP",{"$f":"B52/(B51)","v":3.222641509433962},null,{"$f":"D52/(D51)","v":3.2424242424242427},null,{"$f":"F52/(F51)","v":3.2424242424242427},null,{"$f":"H52/(H51)","v":3.2547528517110269},null,{"$f":"J52/(J51)","v":3.2633587786259541},null,{"$f":"L52/(L51)","v":3.2720306513409958},null,{"$f":"N52/(N51)","v":3.264367816091954}]
[]
["Refrigerant","R717"]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.57,"kW",2.59,"kW",2.62,"kW",2.66,"kW",2.71,"kW",2.79,"kW",2.78,"kW"]
["Condenser",7.47,"kW",7.49,"kW",7.51,"kW",7.51,"kW",7.51,"kW",7.5,"kW",7.49,"kW"]
["COP",{"$f":"B58/(B57)","v":2.9066147859922178},null,{"$f":"D58/(D57)","v":2.8918918918918921},null,{"$f":"F58/(F57)","v":2.8664122137404577},null,{"$f":"H58/(H57)","v":2.8233082706766917},null,{"$f":"J58/(J57)","v":2.7712177121771218},null,{"$f":"L58/(L57)","v":2.6881720430107525},null,{"$f":"N58/(N57)","v":2.6942446043165469}]
[]
[]
[]
[]
["Refrigerant","R290"]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.57,"kW",2.58,"kW",2.6,"kW",2.63,"kW",2.67,"kW",2.73,"kW",2.73,"kW"]
["Gas cooler",8.61,"kW",8.6199999999999992,"kW",8.6199999999999992,"kW",8.6199999999999992,"kW",8.61,"kW",8.61,"kW",8.59,"kW"]
["COP",{"$f":"B67/(B66)","v":3.350194552529183},null,{"$f":"D67/(D66)","v":3.3410852713178292},null,{"$f":"F67/(F66)","v":3.3153846153846152},null,{"$f":"H67/(H66)","v":3.2775665399239542},null,{"$f":"J67/(J66)","v":3.2247191011235952},null,{"$f":"L67/(L66)","v":3.1538461538461537},null,{"$f":"N67/(N66)","v":3.1465201465201464}]
[]
[]
[]
[]
["Refrigerant","R410A"]
["Intermediat temp",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp",2.48,"kW",2.4900000000000002,"kW",2.52,"kW",2.5499999999999998,"kW",2.59,"kW",2.64,"kW",2.63,"kW"]
["Gas cooler",8.19,"kW",8.1999999999999993,"kW",8.2100000000000009,"kW",8.2100000000000009,"kW",8.2100000000000009,"kW",8.1999999999999993,"kW",8.19,"kW"]
["COP",{"$f":"B76/(B75)","v":3.3024193548387095},null,{"$f":"D76/(D75)","v":3.2931726907630519},null,{"$f":"F76/(F75)","v":3.2579365079365084},null,{"$f":"H76/(H75)","v":3.2196078431372555},null,{"$f":"J76/(J75)","v":3.1698841698841704},null,{"$f":"L76/(L75)","v":3.1060606060606055},null,{"$f":"N76/(N75)","v":3.1140684410646386}]

{"sheet":"Best intermediate","index":3,"n_rows":160,"n_cols":16,"rows_kept":160,"cut":false,"hidden":false,"merged":[]}
["Find the best intermediat pressure/temperature"]
[]
[]
["Refrigerant",null,"R717"]
["Evaporator input",null,null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",null,-35,"˚C","Temperature",-33,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"F9","v":70},"%"]
[null,null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,null,"mR717 total",5.0000000000000001E-3,"kg/s",null,null,null,null,null,null,"Temperature",28,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Log p-h diagram"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",1.82,"kW",1.71,"kW",1.63,"kW",1.54,"kW",1.46,"kW",1.41,"kW",1.42,"kW"]
["Gas cooler","kW",7.99,"kW",8.0299999999999994,"kW",8.0399999999999991,"kW",8.0399999999999991,"kW",8.07,"kW",8.1199999999999992,"kW",8.24,"kW"]
["COP",null,{"$f":"C17/C16","v":4.3901098901098905},null,{"$f":"E17/E16","v":4.6959064327485374},null,{"$f":"G17/G16","v":4.9325153374233128},null,{"$f":"I17/I16","v":5.2207792207792201},null,{"$f":"K17/K16","v":5.5273972602739727},null,{"$f":"M17/M16","v":5.7588652482269502},null,{"$f":"O17/O16","v":5.802816901408451}]
[]
[]
["CoolPack"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.6,"kW",2.5,"kW",2.4,"kW",2.2000000000000002,"kW",2.1,"kW",2,"kW",1.8,"kW"]
["Condenser","kW",9.4,"kW",9.4,"kW",9.5,"kW",9.5,"kW",9.5,"kW",9.6,"kW",9.6,"kW"]
["COP",null,{"$f":"C24/(C23)","v":3.6153846153846154},null,{"$f":"E24/(E23)","v":3.7600000000000002},null,{"$f":"G24/(G23)","v":3.9583333333333335},null,{"$f":"I24/(I23)","v":4.3181818181818175},null,{"$f":"K24/(K23)","v":4.5238095238095237},null,{"$f":"M24/(M23)","v":4.8},null,{"$f":"O24/(O23)","v":5.333333333333333}]
[]
[]
["Kolsaker"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.74,"kW",2.77,"kW",2.78,"kW",2.79,"kW",2.79,"kW",2.79,"kW",2.78,"kW"]
["Gas cooler","kW",7.47,"kW",7.49,"kW",7.51,"kW",7.51,"kW",7.51,"kW",7.5,"kW",7.49,"kW"]
["COP",null,{"$f":"C31/(C30)","v":2.7262773722627736},null,{"$f":"E31/(E30)","v":2.7039711191335742},null,{"$f":"G31/(G30)","v":2.7014388489208634},null,{"$f":"I31/(I30)","v":2.6917562724014337},null,{"$f":"K31/(K30)","v":2.6917562724014337},null,{"$f":"M31/(M30)","v":2.6881720430107525},null,{"$f":"O31/(O30)","v":2.6942446043165469}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Refrigerant ",null,"R290"]
[]
["Evaporator input",null,null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",null,-35,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"F48","v":70},"%"]
[null,null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,null,"mR290 total",0.02,"kg/s",null,null,null,null,null,null,"Temperature",30,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Log p-h diagram"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.5,"kW",2.5099999999999998,"kW",2.48,"kW",2.5099999999999998,"kW",2.56,"kW",2.62,"kW",2.79,"kW"]
["Condenser","kW",8.5,"kW",8.5399999999999991,"kW",8.48,"kW",8.48,"kW",8.48,"kW",8.5440000000000005,"kW",8.5399999999999991,"kW"]
["COP",null,{"$f":"C56/C55","v":3.4},null,{"$f":"E56/E55","v":3.402390438247012},null,{"$f":"G56/G55","v":3.4193548387096775},null,{"$f":"I56/I55","v":3.378486055776893},null,{"$f":"K56/K55","v":3.3125},null,{"$f":"M56/M55","v":3.2610687022900762},null,{"$f":"O56/O55","v":3.0609318996415769}]
[]
[]
["CoolPack"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.5,"kW",2.4,"kW",2.2000000000000002,"kW",2.1,"kW",1.9,"kW",1.8,"kW",1.7,"kW"]
["Gas cooler","kW",9.6,"kW",9.4,"kW",9.1999999999999993,"kW",9,"kW",8.8000000000000007,"kW",8.6,"kW",8.4,"kW"]
["COP",null,{"$f":"C63/(C62)","v":3.84},null,{"$f":"E63/(E62)","v":3.916666666666667},null,{"$f":"G63/(G62)","v":4.1818181818181808},null,{"$f":"I63/(I62)","v":4.2857142857142856},null,{"$f":"K63/(K62)","v":4.6315789473684212},null,{"$f":"M63/(M62)","v":4.7777777777777777},null,{"$f":"O63/(O62)","v":4.9411764705882355}]
[]
[]
["Kolsaker"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.57,"kW",2.58,"kW",2.6,"kW",2.63,"kW",2.67,"kW",2.73,"kW",2.73,"kW"]
["Gas cooler","kW",8.61,"kW",8.6199999999999992,"kW",8.6199999999999992,"kW",8.6199999999999992,"kW",8.61,"kW",8.61,"kW",8.59,"kW"]
["COP",null,{"$f":"C70/(C69)","v":3.350194552529183},null,{"$f":"E70/(E69)","v":3.3410852713178292},null,{"$f":"G70/(G69)","v":3.3153846153846152},null,{"$f":"I70/(I69)","v":3.2775665399239542},null,{"$f":"K70/(K69)","v":3.2247191011235952},null,{"$f":"M70/(M69)","v":3.1538461538461537},null,{"$f":"O70/(O69)","v":3.1465201465201464}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Refrigerant",null,"R410A"]
["Evaporator input",null,null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",null,null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar"]
[null,null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,null,"Isentropic efficiency",70,"%",null,null,null,"Isentropic efficiency",{"$f":"F86","v":70},"%"]
[null,null,null,null,"Heat loss",5,"%",null,null,null,null,null,null,"Condenser temperature"]
[null,null,null,null,"mR140A total",0.03,"kg/s",null,null,null,null,null,null,"Temperature",28,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Output",10,"˚C"]
[]
["Log p-h diagram"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.2200000000000002,"kW",2.2999999999999998,"kW",2.5299999999999998,"kW",2.4900000000000002,"kW",2.44,"kW",2.5099999999999998,"kW",2.54,"kW"]
["Condenser","kW",7.92,"kW",7.49,"kW",8.2200000000000006,"kW",8.1,"kW",8.0399999999999991,"kW",8.01,"kW",7.98,"kW"]
["COP",null,{"$f":"C94/C93","v":3.5675675675675671},null,{"$f":"E94/E93","v":3.2565217391304353},null,{"$f":"G94/G93","v":3.2490118577075102},null,{"$f":"I94/I93","v":3.2530120481927707},null,{"$f":"K94/K93","v":3.2950819672131146},null,{"$f":"M94/M93","v":3.1912350597609564},null,{"$f":"O94/O93","v":3.1417322834645671}]
[]
[]
["CoolPack"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.2000000000000002,"kW",2.1,"kW",1.9,"kW",1.8,"kW",1.7,"kW",1.6,"kW",1.5,"kW"]
["Gas cooler","kW",8.5,"kW",8.1999999999999993,"kW",8,"kW",7.8,"kW",7.6,"kW",7.5,"kW",7.3,"kW"]
["COP",null,{"$f":"C101/(C100)","v":3.8636363636363633},null,{"$f":"E101/(E100)","v":3.9047619047619042},null,{"$f":"G101/(G100)","v":4.2105263157894735},null,{"$f":"I101/(I100)","v":4.333333333333333},null,{"$f":"K101/(K100)","v":4.4705882352941178},null,{"$f":"M101/(M100)","v":4.6875},null,{"$f":"O101/(O100)","v":4.8666666666666663}]
[]
[]
["Kolsaker"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.48,"kW",2.4900000000000002,"kW",2.52,"kW",2.5499999999999998,"kW",2.59,"kW",2.64,"kW",2.63,"kW"]
["Gas cooler","kW",8.19,"kW",8.1999999999999993,"kW",8.2100000000000009,"kW",8.2100000000000009,"kW",8.2100000000000009,"kW",8.1999999999999993,"kW",8.19,"kW"]
["COP",null,{"$f":"C108/(C107)","v":3.3024193548387095},null,{"$f":"E108/(E107)","v":3.2931726907630519},null,{"$f":"G108/(G107)","v":3.2579365079365084},null,{"$f":"I108/(I107)","v":3.2196078431372555},null,{"$f":"K108/(K107)","v":3.1698841698841704},null,{"$f":"M108/(M107)","v":3.1060606060606055},null,{"$f":"O108/(O107)","v":3.1140684410646386}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Refrigerant",null,"R744"]
["Evaporator input",null,null,null,"1. Compressor input",null,null,"1. Compressor output",null,null,"2. Compressor input",null,null,"2. Compressor output"]
["Temperature",null,null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C","Temperature",null,"˚C"]
["Pressure",null,null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",null,"bar","Pressure",85,"bar"]
[null,null,null,null,"Power",null,"kW",null,null,null,"Power",null,"kW"]
[null,null,null,null,"Isentropic efficiency",80,"%",null,null,null,"Isentropic efficiency",{"$f":"F124","v":80},"%"]
[null,null,null,null,"Heat loss",5,"%"]
[null,null,null,null,"mR744",2.3300000000000001E-2,"kg/s",null,null,null,null,null,null,"Gas cooler output"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Temperature",10,"˚C"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Pressure",null,"bar"]
[]
["Log p-h diagram"]
["Intermediat temp","˚C",-15,null,-10,null,-5,null,0,null,5,null,10,null,15]
["Comp","kW",2.48,null,2.4300000000000002,null,2.44,null,2.63,null,2.31,null,2.52,null,2.84]
["Condenser","kW",7.39,null,7.32,null,7.32,null,7.46,null,7.08,null,7.25,null,7.55]
["COP",null,{"$f":"C133/C132","v":2.979838709677419},null,{"$f":"E133/E132","v":3.0123456790123457},null,{"$f":"G133/G132","v":3},null,{"$f":"I133/I132","v":2.8365019011406845},null,{"$f":"K133/K132","v":3.0649350649350651},null,{"$f":"M133/M132","v":2.876984126984127},null,{"$f":"O133/O132","v":2.658450704225352}]
[]
[]
["CoolPack"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.68,"kW",2.71,"kW",2.73,"kW",2.73,"kW",2.76,"kW",2.78,"kW",2.79,"kW"]
["Gas cooler","kW",7.28,"kW",7.3,"kW",7.32,"kW",7.33,"kW",7.34,"kW",7.35,"kW",7.35,"kW"]
["COP",null,{"$f":"C140/(C139)","v":2.716417910447761},null,{"$f":"E140/(E139)","v":2.6937269372693726},null,{"$f":"G140/(G139)","v":2.6813186813186816},null,{"$f":"I140/(I139)","v":2.6849816849816852},null,{"$f":"K140/(K139)","v":2.6594202898550727},null,{"$f":"M140/(M139)","v":2.6438848920863309},null,{"$f":"O140/(O139)","v":2.6344086021505375}]
[]
[]
["Kolsaker"]
["Intermediat temp","˚C",-15,"˚C",-10,"˚C",-5,"˚C",0,"˚C",5,"˚C",10,"˚C",15,"˚C"]
["Comp","kW",2.74,"kW",2.77,"kW",2.78,"kW",2.79,"kW",2.79,"kW",2.79,"kW",2.78,"kW"]
["Gas cooler","kW",7.47,"kW",7.49,"kW",7.51,"kW",7.51,"kW",7.51,"kW",7.5,"kW",7.49,"kW"]
["COP",null,{"$f":"C147/(C146)","v":2.7262773722627736},null,{"$f":"E147/(E146)","v":2.7039711191335742},null,{"$f":"G147/(G146)","v":2.7014388489208634},null,{"$f":"I147/(I146)","v":2.6917562724014337},null,{"$f":"K147/(K146)","v":2.6917562724014337},null,{"$f":"M147/(M146)","v":2.6881720430107525},null,{"$f":"O147/(O146)","v":2.6942446043165469}]
[]
[]
[]
[]
[]
[]
[]
["When considering the above values, the best suited value to be used as the intermediat temperature in a two-stage compression in a heat pump should be 5ºC."]
["This is because in the log p-h diagram for R744 and R410A the peak COP was at this temperature. Thereby it is some consistency"]
["There was no peak COP in R717"]
["R290 has a COP peak at 0ºC the log p-h diagram"]
["R744 has a COP peak at  0ºC in CoolPack"]

{"sheet":"Confirm Kolsaker","index":4,"n_rows":64,"n_cols":25,"rows_kept":64,"cut":false,"hidden":false,"merged":[]}
["Confirmation of the one and two stage compression"]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Refrigerant",null,"R717",null,null,"Refrigerant",null,"R717"]
[null,"One-stage Compression",null,null,null,null,"Two-stage Compression"]
[null,"Evaporation temperature",null,-30,"˚C",null,"Evaporation temperature",null,-35,"˚C",null,null,"Log p-h diagram CoolPack",null,null,null,null,null,"Difference in h-value 2 stage"]
[null,"Evaporation pressure",null,{"$f":"r_psatgasT(D10,D12)/100000","v":1.1948575624957021},"bar",null,"Evaporation pressure",null,{"$f":"r_psatgasT(I10,I12)/100000","v":0.93139234305794216},"bar",null,null,"xf","hA",1419.8,"kJ/kg",null,null,null,"Kolsaker","Log p-h diagram",null,"% difference"]
[null,"Temperature in to compressor",null,{"$f":"D12+2","v":-28},"˚C",null,"Temperature in to compressor",null,{"$f":"I12+2","v":-33},"˚C",null,null,"(hC-hF)/(hC-hG)","hB",1762.8,"kJ/kg",null,null,"hA-hB",{"$f":"I26-I16","v":342.90131856034282},{"$f":"O14-O13","v":343},null,{"$f":"(U14-T14)/U14*100","v":2.877009902541821E-2}]
[null,null,null,null,null,null,"1. Compressor",null,null,null,null,null,{"$f":"(O15-O18)/(O15-O19)","v":0.98535625627211743},"hC",1738.19,"kJ/kg",null,null,"hB-hC",{"$f":"I26-I32","v":23.570319557842822},{"$f":"O14-O15","v":24.6099999999999},null,{"$f":"(U15-T15)/U15*100","v":4.2246259331860294}]
[null,"Enthalpy input compressor",null,{"$f":"r_hgastp(D10,D14,D13*100000)/1000","v":1588.8541500219831},"kJ/kg",null,"Enthalpy input compressor",null,{"$f":"r_hgastp(I10,I14,I13*100000)/1000","v":1581.145123837284},"kJ/kg",null,null,null,"hD",1894.2,"kJ/kg",null,null,"hC-hD",{"$f":"I43-I32","v":218.77729455881286},{"$f":"O16-O15","v":156.01},null,-40.232866200123624]
[null,"Entropy",null,{"$f":"R_SgasTP(D10,D14,D13*100000)","v":6643.4283727965294},"J/kgK",null,"Entropy",null,{"$f":"R_SgasTP(I10,I14,I13*100000)","v":6729.9387344969409},"J/kgK",null,null,"COP two stage","hE",245.73,"kJ/kg",null,null,"hD-hE",{"$f":"I43-I47","v":1710.7384160148827},{"$f":"O16-O17","v":1648.47},null,-3.7773460247916328]
[null,"Specific volume",null,{"$f":"R_vgasTP(D10,D14,D13*100000)","v":0.97203217888177396},"m3/kg",null,"Specific volume",null,{"$f":"R_vgasTP(I10,I14,I13*100000)","v":1.226958816968579},"m3/kg",null,null,"(hD-hE)/(xf(hB-hA)+(hD-hC)","hF",{"$f":"O17","v":245.73},"kJ/kg",null,null,"hF-hG",{"$f":"I47-I49","v":27.325728904091818},{"$f":"O17-O19","v":22.179999999999978},null,-23.199859802037171]
[null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"(O16-O17)/(M15*(O14-O13)+(O16-O15))","v":3.337070299954187},"hG",223.55,"kJ/kg",null,null,"hH-hA",{"$f":"I16-I49","v":1199.9558513576617},{"$f":"O13-O19","v":1196.25},null,-0.30978903721309808]
[null,"Condensating temperature",null,28,"˚C",null,"Intermediat temperature",null,5,"˚C",null,null,null,"hH",{"$f":"O19","v":223.55},"kJ/kg",null,null,"COP",{"$f":"I64","v":3.0795748718331111},{"$f":"M19","v":3.337070299954187},null,{"$f":"(U20-T20)/U20*100","v":7.7162122753185933}]
[null,"Condensating pressure",null,{"$f":"r_psatgasT(D10,D20)/100000","v":10.98753082742004},"bar",null,"Intermediat pressure",null,{"$f":"r_psatgasT(I10,I20)/100000","v":5.1564701792426098},"bar"]
[null,"Pressure ration",null,{"$f":"D21/D13","v":9.1956825418339871},null,null,"Intermediat pressure ratio",null,{"$f":"I21/I13","v":5.5363029529670769},null,null,null,null,"mR717",5.0000000000000001E-3,"kg/s"]
[null,"Isentropic efficiency",null,0.7,null,null,"Isentropic efficiency",null,0.7,null,null,null,null,"xf value",{"$f":"1-0.019","v":0.98099999999999998}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Effect of comp",null,"Temp out of comp"]
[null,"Isentropic entalpy",null,{"$f":"R_hgasSP(D10,D17,D21*100000)/1000","v":1924.4370712891191},"kJ/kg",null,"Isentropic entalpy",null,{"$f":"R_hgasSP(I10,I17,I21*100000)/1000","v":1821.176046829524},"kJ/kg",null,null,null,"1.",{"$f":"(O22*O23)*(O14-O13)","v":1.6824149999999998},"kW",127.12,"˚C"]
[null,"Real entropy",null,{"$f":"D16+(D25-D16)/D23","v":2068.258323260749},"kJ/kg",null,"Real entropy",null,{"$f":"I16+(I25-I16)/I23","v":1924.0464423976268},"kJ/kg",null,null,null,"2.",{"$f":"O22*(O16-O15)","v":0.78005000000000002},"kW",186.11,"˚C"]
[null,"Temperature out of compressor",null,{"$f":"R_tgasHP(D10,D26*1000,D21*100000)","v":191.15165573537701},"˚C",null,"Temperature out of compressor",null,{"$f":"R_tgasHP(I10,I26*1000,I21*100000)","v":127.01520023319679},"˚C",null,null,null,"Tot",{"$f":"SUM(O25:O26)","v":2.4624649999999999},"kW",null,null,null,null,"CoolPack","Log p-h","Kolsaker","Diff CoolPack vs Kolsaker","Diff log vss kolsaker"]
[null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(D10,D20)/1000","v":1647.0569069437411},"kJ/kg",null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(I10,I20)/1000","v":1628.9138084843519},"kJ/kg",null,null,null,null,"Effect of gas cooler",null,null,null,null,"Comp  1",{"$f":"N39","v":1.4},{"$f":"O25","v":1.6824149999999998},{"$f":"I59","v":1.6847934653008614},{"$f":"((W28-U28)/W28)*100","v":16.903761272008765},{"$f":"((W28-V28)/W28)*100","v":0.14117251460474273}]
[null,"Subcooling of condenser",null,18,"˚C",null,"2. Compressor",null,null,null,null,null,null,null,{"$f":"O22*(O16-O17)","v":8.2423500000000001},"kW",null,null,null,"Comp2",{"$f":"N40","v":1.3},{"$f":"O26","v":0.78005000000000002},{"$f":"I60","v":1.0946166115228804},{"$f":"(-(W29-U29)/W29)*100","v":18.763043271504987},{"$f":"((W29-V29)/W29)*100","v":28.737606227740415}]
[null,"Enthalpy out of the condenser",null,{"$f":"R_hsatliqT(D10,D20-D29)/1000","v":408.51500138371409},"kJ/kg",null,"Intermediat cooling",null,10,"K",null,null,null,null,"COP-comp effect",null,null,null,null,"Cond.",{"$f":"N38","v":10.1},{"$f":"O29","v":8.2423500000000001},{"$f":"I63","v":8.5594014311061315},{"$f":"(-(W30-U30)/W30)*100","v":17.998905429240704},3.7041308747819635]
[null,null,null,null,null,null,"Temperature in to compressor",null,{"$f":"I27-I30","v":117.01520023319679},"˚C",null,null,null,null,{"$f":"O29/O27","v":3.3471947824639132},null,null,null,null,"COP",{"$f":"N41","v":3.7407407407407405},{"$f":"M19","v":3.337070299954187},{"$f":"I64","v":3.0795748718331111},{"$f":"((U31-W31)/U31)*100","v":17.674731149015837},{"$f":"((V31-W31)/V31)*100","v":7.7162122753185933}]
[null,"Enthalpy in to evaporator",null,{"$f":"D30","v":408.51500138371409},"kJ/kg",null,"Enthalpy input compressor",null,{"$f":"r_hgastp(I10,I31,I21*100000)/1000","v":1900.476122839784},"kJ/kg"]
[null,"Cooling capacity",null,{"$f":"D35*(D16-D32)","v":5.6656279134636902},"kW",null,"Entropy",null,{"$f":"R_SgasTP(I10,I31,I21*100000)","v":6942.532521711405},"J/kgK"]
[null,"Cooling COP",null,{"$f":"D33/D41","v":2.4620961070574667},null,null,"Specific volume",null,{"$f":"R_vgasTP(I10,I31,I21*100000)","v":0.36218738244472148},"m3/kg"]
[null,"Refrigerant fluid mass flow",null,4.7999999999999996E-3,"kg/s"]
[null,"Volume flow",null,{"$f":"D37/3600","v":4.875E-3},"m3/s",null,"Condensating temperature",null,28,"˚C"]
[null,"Volume flow",null,{"$f":"D39*D38","v":17.55},"m3/h",null,"Condensating pressure",null,{"$f":"r_psatgasT(I10,I36)/100000","v":10.98753082742004},"bar",null,null,"Coolpack effects"]
[null,"Volumetric efficiency",null,0.65,null,null,"Pressure ration",null,{"$f":"I37/I21","v":2.1308240803273502},null,null,null,"Condenser",10.1,"kW","Temp out of comp"]
[null,"Cylinder volume",null,27,"m3/h",null,"Pressure ration TOTAL",null,{"$f":"I37/I13","v":11.796887648169664},null,null,null,"Compressor 1",1.4,"kW",122.6,"˚C"]
[null,null,null,null,null,null,"Isentropic efficiency",null,0.7,null,null,null,"Compressor 2",1.3,"kW",201.9,"˚C"]
[null,"Compressor effect",null,{"$f":"D35*(D26-D16)","v":2.3011400315460762},"kW",null,null,null,null,null,null,null,"COP",{"$f":"N38/(N39+N40)","v":3.7407407407407405}]
[null,"Over heating heat",null,{"$f":"D35*(D26-D28)","v":2.0217667983216376},"kW",null,"Isentropic entalpy",null,{"$f":"R_hgasSP(I10,I33,I37*100000)/1000","v":2053.6202290309529},"kJ/kg",null,null,"xf value",{"$f":"1-0.02","v":0.98}]
[null,"Heating capacity",null,{"$f":"D35*(D26-D32)","v":7.9667679450097664},"kW",null,"Real entropy",null,{"$f":"I32+(I42-I32)/I40","v":2119.2534173985969},"kJ/kg"]
[null,"Heating COP",null,{"$f":"D43/D41","v":3.4620961070574667},null,null,"Temperature out of compressor",null,{"$f":"R_tgasHP(I10,I43*1000,I37*100000)","v":211.4323407260953},"˚C"]
[null,null,null,null,null,null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(I10,I36)/1000","v":1647.0569069437411},"kJ/kg"]
[null,"Log p-h diagram in CoolPack",null,null,null,null,"Subcooling of condenser",null,18,"K"]
[null,"h1",1426.62,"kJ/kg",null,null,"Enthalpy out of the condenser",null,{"$f":"R_hsatliqT(I10,I36-I46)/1000","v":408.51500138371409},"kJ/kg"]
[null,"h2",1906.14,"kJ/kg"]
[null,"h3=h4",245.73,"kJ/kg",null,null,"Enthalpy in to evaporator",null,{"$f":"R_HsatliqP(I10,I20*100000)/1000","v":381.18927247962228},"kJ/kg"]
[null,"COP",{"$f":"(C48-C49)/(C48-C47)","v":3.4626501501501488},null,null,null,"Moist vapor - xf",null,{"$f":"(I32-I47)/(I32-I49)","v":0.98201410819976898}]
[null,"Output temp of comp",190.9,"˚C",null,null,"Cooling capacity",null,{"$f":"I53*(I16-I49)","v":6.0037839422000765},"kW"]
[null,null,null,null,null,null,"Cooling COP",null,{"$f":"I51/I61","v":2.1600928888698174}]
[null,null,null,null,null,null,"Refrigerant mass flow",null,{"$f":"I54/I18","v":5.0033373606264238E-3},"kg/s"]
[null,"Coolpack effects",null,null,null,null,"Volume flow",null,{"$f":"I55/3600","v":6.138888888888889E-3},"m3/s"]
[null,"Compressor",2.4,"kW",null,null,"Volume flow",null,{"$f":"I57*I56","v":22.1},"m3/h"]
[null,"Condenser",7.9,"kW",null,null,"Volumetric efficiency",null,0.65]
[null,"COP",{"$f":"C56/C55","v":3.291666666666667},null,null,null,"Cylinder volume",null,34,"m3/h"]
[null,"Output temp of comp",187.3,"˚C"]
[null,null,null,null,null,null,"Compressor effect 1. compressor",null,{"$f":"(I53*I50)*(I26-I16)","v":1.6847934653008614},"kW"]
[null,null,null,null,null,null,"Compressor effect 2. compressor",null,{"$f":"I53*(I43-I32)","v":1.0946166115228804},"kW"]
[null,null,null,null,null,null,"Compressor effect TOTAL",null,{"$f":"I60+I59","v":2.7794100768237415},"kW"]
[null,null,null,null,null,null,"Over heating heat",null,{"$f":"(I53*(I43-I45))+((I53/2)*(I26-I28))","v":3.1008825091153907},"kW"]
[null,null,null,null,null,null,"Heating capacity",null,{"$f":"(I53*(I43-I47))","v":8.5594014311061315},"kW"]
[null,null,null,null,null,null,"Heating COP",null,{"$f":"I63/I61","v":3.0795748718331111}]

{"sheet":"Kolsaker sheet","index":5,"n_rows":60,"n_cols":19,"rows_kept":60,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
["Refrigerant",null,"R717",null,null,null,null,"Refrigerant",null,"R717",null,null,null,null,null,"Refrigerant",null,"R717"]
["One-stage Compression",null,null,null,null,null,null,"Two-stage Compression",null,null,null,null,null,null,null,"Two-stage Compression"]
["Evaporation temperature",null,-30,"˚C",null,null,null,"Evaporation temperature",null,-35,"˚C",null,null,null,null,"Evaporation temperature",null,-35,"˚C"]
["Evaporation pressure",null,{"$f":"r_psatgasT(C5,C7)/100000","v":1.1948575624957021},"bar",null,null,null,"Evaporation pressure",null,{"$f":"r_psatgasT(J5,J7)/100000","v":0.93139234305794216},"bar",null,null,null,null,"Evaporation pressure",null,{"$f":"r_psatgasT(R5,R7)/100000","v":0.93139234305794216},"bar"]
["Temperature in to compressor",null,{"$f":"C7+5","v":-25},"˚C",null,null,null,"Temperature in to compressor",null,{"$f":"J7+5","v":-30},"˚C",null,null,null,null,"Temperature in to compressor",null,{"$f":"R7+5","v":-30},"˚C"]
["Enthalpy input compressor",null,{"$f":"r_hgastp(C5,C9,C8*100000)/1000","v":1595.8726945394619},"kJ/kg",null,null,null,"1. Compressor",null,null,null,null,null,null,null,"1. Compressor"]
["Entropy",null,{"$f":"R_SgasTP(C5,C9,C8*100000)","v":6671.8737034614287},"J/kgK",null,null,null,"Enthalpy input compressor",null,{"$f":"r_hgastp(J5,J9,J8*100000)/1000","v":1588.0418439946041},"kJ/kg",null,null,null,null,"Enthalpy input compressor",null,{"$f":"r_hgastp(R5,R9,R8*100000)/1000","v":1588.0418439946041},"kJ/kg"]
["Specific volume",null,{"$f":"R_vgasTP(C5,C9,C8*100000)","v":0.98560605486926334},"m3/kg",null,null,null,"Entropy",null,{"$f":"R_SgasTP(J5,J9,J8*100000)","v":6758.4680218419044},"J/kgK",null,null,null,null,"Entropy",null,{"$f":"R_SgasTP(R5,R9,R8*100000)","v":6758.4680218419044},"J/kgK"]
[null,null,null,null,null,null,null,"Specific volume",null,{"$f":"R_vgasTP(J5,J9,J8*100000)","v":1.2441551903651089},"m3/kg",null,null,null,null,"Specific volume",null,{"$f":"R_vgasTP(R5,R9,R8*100000)","v":1.2441551903651089},"m3/kg"]
["Condensating temperature",null,28,"˚C"]
["Condensating pressure",null,{"$f":"r_psatgasT(C5,C14)/100000","v":10.98753082742004},"bar",null,null,null,"Intermediat temperature",null,5,"˚C",null,null,null,null,"Intermediat temperature",null,5,"˚C"]
["Pressure ration",null,{"$f":"C15/C8","v":9.1956825418339871},null,null,null,null,"Intermediat pressure",null,{"$f":"r_psatgasT(J5,J15)/100000","v":5.1564701792426098},"bar",null,null,null,null,"Intermediat pressure",null,{"$f":"r_psatgasT(R5,R15)/100000","v":5.1564701792426098},"bar"]
["Isentropic efficiency",null,0.7,null,null,null,null,"Intermediat pressure ratio",null,{"$f":"J16/J8","v":5.5363029529670769},null,null,null,null,null,"Intermediat pressure ratio",null,{"$f":"R16/R8","v":5.5363029529670769}]
[null,null,null,null,null,null,null,"Isentropic efficiency",null,0.7,null,null,null,null,null,"Isentropic efficiency",null,0.7]
["Isentropic entalpy",null,{"$f":"R_hgasSP(C5,C11,C15*100000)/1000","v":1936.061700872554},"kJ/kg"]
["Real entropy",null,{"$f":"C10+(C19-C10)/C17","v":2081.8569893010222},"kJ/kg",null,null,null,"Isentropic entalpy",null,{"$f":"R_hgasSP(J5,J12,J16*100000)/1000","v":1831.4045754201779},"kJ/kg",null,null,null,null,"Isentropic entalpy",null,{"$f":"R_hgasSP(R5,R12,R16*100000)/1000","v":1831.4045754201779},"kJ/kg"]
["Temperature out of compressor",null,{"$f":"R_tgasHP(C5,C20*1000,C15*100000)","v":196.57856047216009},"˚C",null,null,null,"Real entropy",null,{"$f":"J11+(J20-J11)/J18","v":1935.702888888281},"kJ/kg",null,null,null,null,"Real entropy",null,{"$f":"R11+(R20-R11)/R18","v":1935.702888888281},"kJ/kg"]
["Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(C5,C14)/1000","v":1647.0569069437411},"kJ/kg",null,null,null,"Temperature out of compressor",null,{"$f":"R_tgasHP(J5,J21*1000,J16*100000)","v":131.9461674529459},"˚C",null,null,null,null,"Temperature out of compressor",null,{"$f":"R_tgasHP(R5,R21*1000,R16*100000)","v":131.9461674529459},"˚C"]
["Subcooling of condenser",null,18,"K",null,null,null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(J5,J15)/1000","v":1628.9138084843519},"kJ/kg",null,null,null,null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(R5,R15)/1000","v":1628.9138084843519},"kJ/kg"]
["Enthalpy out of the condenser",null,{"$f":"R_hsatliqT(C5,C14-C23)/1000","v":408.51500138371409},"kJ/kg",null,null,null,"2. Compressor",null,null,null,null,null,null,null,"2. Compressor"]
[null,null,null,null,null,null,null,"Intermediat cooling",null,10,"K",null,null,null,null,"Intermediat cooling",null,10,"K"]
["Enthalpy in to evaporator",null,{"$f":"C24","v":408.51500138371409},"kJ/kg",null,null,null,"Temperature in to compressor",null,{"$f":"J22-J25","v":121.9461674529459},"˚C",null,null,null,null,"Temperature in to compressor",null,{"$f":"R22-R25","v":121.9461674529459},"˚C"]
["Cooling capacity",null,{"$f":"C29*(C10-C26)","v":2.2839067213046178},"kW",null,null,null,"Enthalpy input compressor",null,{"$f":"r_hgastp(J5,J26,J16*100000)/1000","v":1912.0877826648009},"kJ/kg",null,null,null,null,"Enthalpy input compressor",null,{"$f":"r_hgastp(R5,R26,R16*100000)/1000","v":1912.0877826648009},"kJ/kg"]
["Cooling COP",null,{"$f":"C27/C35","v":2.4432017782350437},null,null,null,null,"Entropy",null,{"$f":"R_SgasTP(J5,J26,J16*100000)","v":6972.1066612992099},"J/kgK",null,null,null,null,"Entropy",null,{"$f":"R_SgasTP(R5,R26,R16*100000)","v":6972.1066612992099},"J/kgK"]
["Refrigerant fluid mass flow",null,{"$f":"C30/C12","v":1.923520380142965E-3},"kg/s",null,null,null,"Specific volume",null,{"$f":"R_vgasTP(J5,J26,J16*100000)","v":0.36709586465217148},"m3/kg",null,null,null,null,"Specific volume",null,{"$f":"R_vgasTP(R5,R26,R16*100000)","v":0.36709586465217148},"m3/kg"]
["Volume flow",null,{"$f":"C31/3600","v":1.8958333333333334E-3},"m3/s"]
["Volume flow",null,{"$f":"C33*C32","v":6.8250000000000002},"m3/h",null,null,null,"Condensating temperature",null,28,"˚C",null,null,null,null,"Condensating temperature",null,28,"˚C"]
["Volumetric efficiency",null,0.65,null,null,null,null,"Condensating pressure",null,{"$f":"r_psatgasT(J5,J31)/100000","v":10.98753082742004},"bar",null,null,null,null,"Condensating pressure",null,{"$f":"r_psatgasT(R5,R31)/100000","v":10.98753082742004},"bar"]
["Cylinder volume",null,10.5,"m3/h",null,null,null,"Pressure ration",null,{"$f":"J32/J16","v":2.1308240803273502},null,null,null,null,null,"Pressure ration",null,{"$f":"R32/R16","v":2.1308240803273502}]
[null,null,null,null,null,null,null,"Pressure ration TOTAL",null,{"$f":"J32/J8","v":11.796887648169664},null,null,null,null,null,"Pressure ration TOTAL",null,{"$f":"R32/R8","v":11.796887648169664}]
["Compressor effect",null,{"$f":"C29*(C20-C10)","v":0.93480069540326716},"kW",null,null,null,"Isentropic efficiency",null,0.7,null,null,null,null,null,"Isentropic efficiency",null,0.7]
["Over heating heat",null,{"$f":"C29*(C20-C22)","v":0.83634681970206981},"kW"]
["Heating capacity",null,{"$f":"C29*(C20-C26)","v":3.2187074167078848},"kW",null,null,null,"Isentropic entalpy",null,{"$f":"R_hgasSP(J5,J28,J32*100000)/1000","v":2067.2590058195842},"kJ/kg",null,null,null,null,"Isentropic entalpy",null,{"$f":"R_hgasSP(R5,R28,R32*100000)/1000","v":2067.2590058195842},"kJ/kg"]
["Heating COP",null,{"$f":"C37/C35","v":3.4432017782350437},null,null,null,null,"Real entropy",null,{"$f":"J27+(J37-J27)/J35","v":2133.7609586002054},"kJ/kg",null,null,null,null,"Real entropy",null,{"$f":"R27+(R37-R27)/R35","v":2133.7609586002054},"kJ/kg"]
["pluss (+) 2 kW water heating",null,{"$f":"(C37+2)/(C35+2)","v":1.7782152719541962},null,null,null,null,"Temperature out of compressor",null,{"$f":"R_tgasHP(J5,J38*1000,J32*100000)","v":217.165560977301},"˚C",null,null,null,null,"Temperature out of compressor",null,{"$f":"R_tgasHP(R5,R38*1000,R32*100000)","v":217.165560977301},"˚C"]
[null,null,null,null,null,null,null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(J5,J31)/1000","v":1647.0569069437411},"kJ/kg",null,null,null,null,"Enthalpy on the dewpoint line",null,{"$f":"R_hsatgasT(R5,R31)/1000","v":1647.0569069437411},"kJ/kg"]
[null,null,null,null,null,null,null,"Subcooling of condenser",null,18,"K",null,null,null,null,"Subcooling of condenser",null,18,"K"]
[null,null,null,null,null,null,null,"Enthalpy out of the condenser",null,{"$f":"R_hsatliqT(J5,J31-J41)/1000","v":408.51500138371409},"kJ/kg",null,null,null,null,"Enthalpy out of the condenser",null,{"$f":"R_hsatliqT(R5,R31-R41)/1000","v":408.51500138371409},"kJ/kg"]
[]
[null,null,null,null,null,null,null,"Enthalpy in to evaporator",null,{"$f":"R_HsatliqP(J5,J15*100000)/1000","v":381.18927247962228},"kJ/kg",null,null,null,null,"Enthalpy in to evaporator",null,{"$f":"R_HsatliqP(R5,R15*100000)/1000","v":381.18927247962228},"kJ/kg"]
[null,null,null,null,null,null,null,"Moist vapor - xf",null,{"$f":"(J27-J42)/(J27-J44)","v":0.98215052877621112},null,null,null,null,null,"Moist vapor - xf",null,{"$f":"(R27-R42)/(R27-R44)","v":0.98215052877621112}]
[null,null,null,null,null,null,null,"Cooling capacity",null,{"$f":"J48*(J11-J44)","v":1.6228676655571947},"kW",null,null,null,null,"Cooling capacity",null,{"$f":"R48*(R11-R44)","v":1.6228676655571947},"kW"]
[null,null,null,null,null,null,null,"Cooling COP",null,{"$f":"J46/J56","v":2.1431205121109258},null,null,null,null,null,"Cooling COP",null,{"$f":"R46/R56","v":2.1197611655198365}]
[null,null,null,null,null,null,null,"Refrigerant mass flow",null,{"$f":"J49/(J13+J29)","v":1.3447107822954568E-3},"kg/s",null,null,null,null,"Refrigerant mass flow",null,{"$f":"R49/(R13+R29)","v":1.3447107822954568E-3},"kg/s"]
[null,null,null,null,null,null,null,"Volume flow",null,{"$f":"J50/3600","v":2.166666666666667E-3},"m3/s",null,null,null,null,"Volume flow",null,{"$f":"R50/3600","v":2.166666666666667E-3},"m3/s"]
[null,null,null,null,null,null,null,"Volume flow",null,{"$f":"J52*J51","v":7.8000000000000007},"m3/h",null,null,null,null,"Volume flow",null,{"$f":"R52*R51","v":7.8000000000000007},"m3/h"]
[null,null,null,null,null,null,null,"Volumetric efficiency",null,0.65,null,null,null,null,null,"Volumetric efficiency",null,0.65]
[null,null,null,null,null,null,null,"Cylinder volume",null,12,"m3/h",null,null,null,null,"Cylinder volume",null,12,"m3/h"]
[]
[null,null,null,null,null,null,null,"Compressor effect 1. compressor",null,{"$f":"(J48*J45)*(J21-J11)","v":0.45915886438899156},"kW",null,null,null,null,"Compressor effect 1. compressor",null,{"$f":"(R48)*(R21-R11)","v":0.46750355565263224},"kW"]
[null,null,null,null,null,null,null,"Compressor effect 2. compressor",null,{"$f":"J48*(J38-J27)","v":0.29808630982601625},"kW",null,null,null,null,"Compressor effect 2. compressor",null,{"$f":"R48*(R38-R27)","v":0.29808630982601625},"kW"]
[null,null,null,null,null,null,null,"Compressor effect TOTAL",null,{"$f":"J55+J54","v":0.75724517421500781},"kW",null,null,null,null,"Compressor effect TOTAL",null,{"$f":"R55+R54","v":0.76558986547864849},"kW"]
[null,null,null,null,null,null,null,"Over heating heat",null,{"$f":"(J48*(J38-J40))+((J48/2)*(J21-J23))","v":0.86074747820416819},"kW",null,null,null,null,"Over heating heat",null,{"$f":"(R48*(R38-R40))+((R48/2)*(R21-R23))","v":0.86074747820416819},"kW"]
[null,null,null,null,null,null,null,"Heating capacity",null,{"$f":"(J48*(J38-J42))","v":2.3199568407806619},"kW",null,null,null,null,"Heating capacity",null,{"$f":"(R48*(R38-R42))","v":2.3199568407806619},"kW"]
[null,null,null,null,null,null,null,"Heating COP",null,{"$f":"J58/J56","v":3.0636799279515077},null,null,null,null,null,"Heating COP",null,{"$f":"R58/R56","v":3.0302867702281033}]
[null,null,null,null,null,null,null,"pluss (+) 2 kW water heating",null,{"$f":"(J58+2)/(J56+2)","v":1.5667655822484343},null,null,null,null,null,"pluss (+) 2 kW water heating",null,{"$f":"(R58+2)/(R56+2)","v":1.562038136856202}]